## Slide 1
Programmable Logic Controllers - Programming Automates Programmables - programmation
Speicherprogrammierbare Steuerungen - Programmierung
Prof. Dr. H. Kirrmann
ABB Research Center, Baden, Switzerland
Industrial Automation
Automation Industrielle Industrielle Automation
2.3
lim
TIT
TIT_REF_TAB
N_GT
POST_START_TIMER_MOD
100
0
FAULT_STATE[tit1_oor]
FAULT_STATE[tit2_oor]
OR
TIT_RATE_LIM_DN
TIT_RATE_LIM_UP
TIT_ERROR
TIT_REF_MAX_START
WFD_TIT
PID
K_TIT
P
TD_TIT
D
MAX_INT
I
17.3

## Slide 2: Contents
2.2 Operation of PLCs
2.3 Programming of the PLC
2.3.1 Ladder Logic 2.3.2 Function blocks 2.3.3 Sequential Logic 2.3.4 IEC 1131
2.2.1 Evolution of the PLC 2.2.2 Classification
2.2.3 Measurement and Input/Output
2.1 Instrumentation
2.1.1 Binary Instruments
2.1.2 Analogue Instruments
2.1.3 P&ID

## Slide 3: Continuous Plant (reminder)
Example: traction motors, ovens, pressure vessel,...
The time constant of the control system must be at least one order of
magnitude smaller than the smallest time constant of the plant.
F(p) =
y
x
The state of continuous plants is described by continuous (analog) state
variables like temperature, voltage, speed, etc.
Continuous plants are normally reversible and monotone.
This is the condition to allow their regulation.
There exist a fixed relationship between input and output,
described by a continuous model in form of a transfer function F.
This transfer function can be expressed by a set of differential equations.
If equations are linear, the transfer function may be given as Laplace or
Z-transform.
time
y
(1+Tp)
(1+T1p + T2 p2)
the principal task of the control system for a continuous plant is its regulation.

## Slide 4: Analog building blocks for continuous control
Basic blocks
Summator / Subtractor Multiplier / Divider Integrator / Differentiator Filter Minimal value, Maximum value Radix Function generator
Regulation Functions
P, PI, PID, PDT2 controller Fixed set-point Ratio and multi-component regulation Parameter variation / setting 2-point regulation 3-point regulation Output value limitation Ramp generator Adaptive regulation Drive Control

## Slide 5: Discrete Plant (reminder)
Examples: Elevators,
traffic signaling,
warehouses, etc.
Discrete plants are normally reversible, but not monotone, i.e. negating the
event which caused a transition will not revert the plant to the previous state.
Example: an elevator don't return to the previous floor when the button is released.
Discrete plants are described by finite state machines, Petri nets or computer programs.
The plant is described by variables which take well-defined, non-overlapping values. The transition from one state to another is abrupt, it is caused by an external event.
main task of a control system with discrete plants is its sequential control.
Notes: The control system must provide stimuli faster than the outer world does.

## Slide 6: Functions of PLCs for discrete plants
logical combinations (AND, OR, NOT, EXOR) Flip-flop Selector m-out-of-n
Multiplexer m-to-n Timer Counter Memory Sequencing
Basic blocks
Display
Manual input, touchscreen
Safety blocks (interlocking)
Logging
Elaborated blocks
Alarm signaling

## Slide 7: Discrete Control
A
B
Out = A · B
B
NOT C
A
Out = (A + B) · C
sequential, memory-based
combinatorial, memoryless
ladder
logic
e.g. GRAFCET
e.g. ladder logic

## Slide 8: Real-Time languages
Extend procedural languages to express time
(“introduce programming constructs to
influence scheduling and control flow”)
languages developed for cyclic
execution and real-time
("application-oriented languages")
ladder logic
function block language
instruction lists
GRAFCET
SDL
etc...
•
•
•
•
•
wide-spread in the control industry
ADA
Real-Time Java
MARS (TU Wien)
Forth
“C” with real-time features
etc…
could not impose themselves
•
•
•
•
•
•

## Slide 9: The five IEC 61131-3 Programming languages
Structured Text (ST)
VAR CONSTANT X : REAL := 53.8 ;
Z : REAL; END_VAR
VAR aFB, bFB : FB_type; END_VAR
bFB(A:=1, B:=‘OK’);
Z := X - INT_TO_REAL (bFB.OUT1);
IF Z>57.0 THEN aFB(A:=0, B:=“ERR”);
ELSE aFB(A:=1, B:=“Z is OK”);
END_IF
Ladder Diagram (LD)
AUTO
MAN_ON
ACT
CALC1
CALC
IN1
IN2
OUT
PUMP
http://www.isagraf.com
Function Block Diagram (FBD)
CALC1
CALC
IN1
IN2
OUT
PUMP
AUTO
MAN_ON
ACT
>=1
DI
V
DO
V
Instruction List (IL)
A: LD %IX1 (* PUSH BUTTON *)
ANDN %MX5 (* NOT INHIBITED *)
ST %QX2 (* FAN ON *)
Sequential Flow Chart (SFC)
START STEP
T1
T2
D1_READY
D2_READY
STEP A
ACTION D1
N
D
ACTION D2
STEP B
D3_READY
D4_READY
ACTION D3
N
D
ACTION D4
T3

## Slide 10: Ladder logic (1)
The ladder logic is the oldest programming language for PLC
it bases directly on the relay intuition of the electricians.
it is widely in use outside Europe

## Slide 11: Ladder logic (2)
(Kontaktplansprache, language à contacts)
The contact plan or "ladder logic" language allows an easy transition from the traditional relay logic diagrams to the programming of binary functions.
It is well suited to express combinational logic
It is however not powerful enough for process control programming (there are no analog elements).
The main ladder logic symbols represent the elements:
make contact
break contact
relay coil

## Slide 12: Ladder logic (3)
Binary combinations are expressed by series and parallel relay contact:
+
01
02
50
Coil 50 is active (current flows) when 01 is active and 02 is not.
01
02
50
Series
+
01
50
02
Coil 50 is active (current flows) when 01 is active or 02 is not.
Parallel
ladder logic representation
"CMOS" equivalent
01
02
50

## Slide 13: Ladder logic (4)
The ladder logic is more intuitive for complex binary expressions than literal languages
50
1
2
3
4
5
6
!N 1 & 2 STR 3 &N 4 STR N 5
& 6 / STR & STR = 50
50
0
1
4
5
6
7
2
3
10
11
12
!0 & 1 STR 2 & 3 / STR STR 4
& 5 STR N 6 & 7
/ STR & STR STR 10
& 11 / STR & 12 = 50

## Slide 14: Ladder logic (5)
Ladder logic stems from the time of the relay technology.
With the PLCs replacing relays, the opened possibilities cannot be expressed
any more in relay terms.
The contact plan language was extended to express functions:
literal expression:
!00 & 01 FUN 02 = 200
200
FUN 02
01
00
The intuition of contacts and coil gets lost.
The introduction of «functions» which influence the control flow itself, is
problematic.
The contact plan is - mathematically - a functional representation.
The introduction of a more or less hidden control of the flow destroys the
freedom of side effects and makes programs difficult to read.

## Slide 15: Ladder logic (6)
!02 FUN00 200
!N200 FUN06
!N55 = 55
FUN07
Example:
02
FUN
00
200
200
FUN 06
55
FUN 07
55
A "1" signal at input 02 is transformed by FUN00 in a pulse 200 of one cycle time.
As a consequence, the program part !N55=55 is executed exactly once, i.e.
mark 55 is inverted (toggled).
The toggle effect appears for each "0-1" transition of the input signal.

## Slide 16: Function Block Languages (1)
The function block languages express combinatorial
programs in a more elaborate way than ladder logic.
They draw on a large variety of predefined and custom functions
(Also called "Function Chart" or "Function Plan")

## Slide 17: Function Block Languages (2)
&
A
B
C
Trigger
T
&
Running
Reset
S
R
Spin
Function blocks is a graphical programming language, which is akin to the electrical and block diagrams of the analog and digital technique.
It mostly expresses combinatorial logic, but its blocks may have a memory
(e.g. flip-flops).
Example 1:
Example 2:
external inputs
external outputs

## Slide 18: Function Block elements (3)
PID
"continuously"
executing block,
independent,
no side effects
set point
measurement
motor
parameters
The block is defined by its:
• Data flow interface (number and type of input/output signals)
• Black-Box-Behavior (functional semantic, e.g. in textual form).
Connections that carry a pseudo-continuous data flow.
Connects the function blocks.
Signals
Function block
(set point)
(set point)
set point
Example
Example

## Slide 19: Data Types
BYTE
WORD
DWORD
SINT
USINT
INT
UINT
DINT
UDINT
REAL
LREAL
binary types:
analog types:
user-defined structured types are supported in the textual language (ST) only
BOOL BYTE WORD DWORD
1 8 16 32
1 8 16 signed integer 16 unsigned integer 16 integer unsigned integer double integer unsigned double integer floating 32 floating 64
Function blocks are typed - the types of connection, input and output must match.
The types are the same as in the Structured Text Language

## Slide 20: Function Block Example

## Slide 21: Function Block rules
There exist exactly two rules for connecting function blocks by signals
(this is the actual programming):
Each signal is connected to exactly one source.
This source can be the output of a function block or a plant signal.
The type of the output pin, the type of the input pin and the signal type
must be identical.
•
•
For convenience, the function plan should be drawn so the signals flow from left
to right and from top to bottom. Some editors impose additional rules.
Retroactions are exception to this rule. In this case, the signal direction is
identified by an arrow. (Some editors forbid retroactions).
a
b
y
x
z

## Slide 22: Function Block behaviour specification
Time Diagram:
0 T
T
x
y
y
x
S
R
x1
0
0
1
1
x2
0
0
1
1
y
previous state
0
1
1
Truth Table:
Textual Description:
Mathematical Formula:
Computer Program:
another Function block !
preferibly in structured text

## Slide 23: Function Block decomposition
A function block describes a
data flow interface
.
Its
body
can be implemented differently:
The body is implemented in an external language
(microcode, assembler, java, 1131 ST):
Elementary block
The body is realized as a function block program
.
Each input (output) pin of the interface is implemented as
exactly one input (output) of the function block.
All signals must appear at the interface to garantee
freedom from
side effects
.
Compound block
procedure xy(a,b:BOOLEAN; VAR b,c: BOOLEAN);
begin
......
....
end xy;
=
=

## Slide 24: Function Block segmentation
An application program is decomposed into segments for easier reading.
• Within a segment, the connections are represented
graphically
.
• Between the segments, the connections are expressed by
signal names
.

## Slide 25: Execution of Function Blocks
F1
A
B
X01
F2
X01
X
F3
B
C
X02
F4
X
X02
Y
Machine Code:
function
input1
input2
output
A
F1
F2
B
F4
Y
X01
X02
F3
C
X
Segment
The function blocks are
translated to a machine code
(intermediate code, IL),
that is either interpreted or
compiled to assembly language

## Slide 26: Input-Output of Function Blocks
execute
individual period
I
O
X
I
O
X
I
O
X
read
inputs
write
outputs
Run-time:
The function blocks are executed cyclically.
• all inputs are read from memory or from the plant (possibly cached)
• the segment is executed
• the results are written into memory or to the plant (possibly to a cache)
The order of execution of the blocks generally does not matter.
To speed up algorithms and avoid cascading, it is helpful to impose an
execution order to the blocks.
The different segments may be assigned a different individual period.
time

## Slide 27: Function Block library
The programmer chooses the blocks in a block library, similarly to the
hardware engineer who chooses CMOS-logic out of the catalogue.
This library indicates the pinning of each block, its semantics and the execution time.
The programmer may extend the library by defining function block macros out of
library elements.
If some blocks are often used, they will be programmed in an external language
(e.g. “C”, microcode).

## Slide 28: IEC 61131-3 library (extract)
the number of inputs or outputs and their type is restricted.
The execution time of each block depends on the number of inputs and on the processor

## Slide 29: Example: Tooth saw generator
exercise: build a tooth-saw (asymmetric) generator with
the IEC 61131 elements of the preceding page

## Slide 30: Sawtooth FBD

## Slide 31: Program configuration
The programmer divides the program into tasks (sometimes called pages or segments),
which may be executed each with a different period.
The loadable program is built by means of a configurator, which assigns each page an
execution period and builds the whole program into a runnable task.
Since the execution time of each block is fixed, the programmer has control over the
execution time.
Event-driven operations are encapsulated into blocks, e.g. for transmitting messages.
If the execution time of these tasks cannot be bound, they are executed in background.
The periodic execution always has the highest priority.

## Slide 32: Sequential Flow Chart (SFC)
START STEP
T1
T2
ACTION D1
N
D1_READY
D
ACTION D2
D2_READY
STEP A
STEP B

## Slide 33: Sequential Flow Chart
Ec = ((varX & varY) | varZ)
The sequential program consists of states connected by transitions.
A state is activated by the presence of a token (the corresponding variable becomes TRUE).
The token leaves the state when the transition condition (event) on the state output is true.
Only one transition takes place at a time, the execution period is a configuration parameter
token
Sa
Sb
"1"
Ea
Sc
Eb
transitions
states
event condition
("1" = always true)
example transition condition
example: Sc is true, S0, Sa, Sb are false
S0

## Slide 34: Initial state
State which come into existence with a token are called initial states.
All initial states receive exactly one token, the other states receive none.
Initialization takes place explicitly at start-up.
In some systems, initialization may be triggered in a user programm
(initialization pin in a function block).

## Slide 35: Switch and parallel execution
Eb
Sa
Sb
"1"
Ea
Se
token switch
: the token crosses the first active
transition (at random if both Ea and Eb are true)
Ec
token forking
: when the transition Ee is true, the token
is replicated to all connected states
Ed
token join
: when all tokens are present,
and the transition Ef is true, one single token is forwarded.
Ee
Sc
Sd
Sf
Sg
Ef

## Slide 36: P1, N and P0 actions
P1
State1_P1:do at enter
N
State1_N:do while
P0
State1_P0:do at leave
State1
P1 (pulse raise) action is executed once when the state is entered
P0 (pulse fall) action is executed once when the state is left
N (non-stored) action is executed continuously while the token is in the state
P1 and P0 actions could be replaced by additional states.
The actions are described by a code block written e.g. in Structured Text.

## Slide 37: Exercise
initially: let vehicle until it touches I0 at reduced speed and open the trap for 5s (empty the vehicle).
1 - Let the vehicle move from I0 to I3
Speed = 5 cm/s between I0 and I1 or between I2 and I3, speed = 1 m/s between I1 and I2.
2 - Stop the vehicle when it reaches I3.
3 - Open the tank during 5s.
4- Go back to I0
5 - Open the trap and wait 5s.
repeat above steps indefinitely
In2
In3
Speed = {+20: +1 m/s; +1: +5 cm/s}
negative values: opposite direction
Generates “1” as long as the tag of the vehicle (1cm) is over the sensor.
Register = {0: closed; 1: open}
In0
In1
Variables:
Input: In0, In1, In2, In3;
Output:
+speed
Trap = {0: closed; 1: open}
Register = {0: closed; 1: open}

## Slide 38: Wagon SFC

## Slide 39: Complex structures
Problems with general networks:
deadlocks
uncontrolled token multiplication
These general rules serve to build networks, termed by DIN and IEC as
flow charts
Solution:
assistance through the flow chart editor.

## Slide 40: Building subprograms
::=
::=
OR:
OR:
OR:
OR:
T-element
S-element
state
S-sequence
parallel paths
transition
T-sequence
alternative paths
loop
OR:
The meta-symbols T and S define structures - they may not appear
as elements in the flow chart.
A flow chart may only contain the terminal symbols: state and transition

## Slide 41: Sequential Chart rules
The input and output flow of a state are always in the same vertical line (simplifies structure)
Alternative paths are drawn such that no path is placed in the vertical flow (otherwise would mean this is a preferential path)
intentional displacement to
avoid optical preference of a
path.
Priority:
• The alternative path most to the left has the
highest priority, priority decreases towards the right.
• Loop: exit has a higher priority than loopback.

## Slide 42: Structuring
Every flow chart without a token generator may be redrawn as a
structured flow chart (by possibly duplicating program parts)
A
B
C
a
b
d
c
Not structured
A
B
C
a
b
a
b
B'
A'
d
c
d
structured

## Slide 43: Exception handling
Not foreseen in IEC61331 - but supported by some editors
as usual
OR
::=
::=
OR
E-path
exception
E-sequence
Semantics
All states which lie in alternative paths to the exception are precursor states to the exception.
What happens when a block is incapable of executing? (e.g. divide-by-zero)

## Slide 44: Exception handling
Example
Exception Nesting:
Exception handling is a neglected issue. However, exceptions most often arise
from incomplete and misunderstood specifications, catching them afterwards is symptom cure.

## Slide 45: Function blocks And Flow Chart
Function Blocks:
Continuous (time) control
Flow Charts:
Discrete (time) Control
Many PLC applications mix continuous and discrete control.
A PLC may execute alternatively function blocks and flow charts.
A communication between these program parts must be possible.
Principle:
The flow chart taken as a whole can be considered a function
block with binary inputs (transitions) and binary outputs (states).

## Slide 46: Executing Flow Charts As blocks
A function block may be implemented in three different ways:
procedure
xy(...);
begin
...
end xy;
extern
function blocks
flow chart
Function blocks and flow chart communicate over binary signals.

## Slide 47: Flow Charts Or Function blocks ?
A task can sometimes be written indifferently as function blocks or as flow chart.
The application may decide which representation is more appropriate:
c
d
"1"
b
a
a
b
c
d
Flow Chart
Function Block
NOT
S
R

## Slide 48: Flow Charts Or Blocks ? (2)
In this example, flow chart seems to be more appropriate:
A
B
C
"1"
a
b
c
S
R
≥
&
S
R
&
S
R
&
init
a
b
c
A
B
C
Flow Chart
Function Blocks

## Slide 49: Assessment
Which are programming languages defined in IEC 61331 and for what are they used ?
In a function block language, which are the two elements of programming ?
How is a PLC program executed and why is it that way ?
Draw a ladder diagram and the corresponding function chart.
Draw a sequential chart implementing a 2-bit counter
Program a saw tooth waveform generator with function blocks
How are inputs and outputs to the process treated in a function chart language ?
Program a sequencer for a simple chewing-gum coin machine
Program a ramp generator for a ventilator speed control (soft start and stop in 5s)